## Slide 1: CRYOGENIC SYSTEM
TIMELINE MEETING
2-22-2011

## Slide 2: 12 Oclock Cryo Control Rack Power:

## Slide 3: 12 Oclock Cryo Control Rack Power:
PLC alarm for 12 oclock racks
Sector 12, 1012B, Sector 11
Outage at 11:39 PM 2/20 Sunday
Power back at 1:30 AM 2/21 Monday
Recovery: Refill recoolers
Initial diagnosis: 480V power lost a phase
Subsequent: UPS failure, bypass switch not working