## Slide 1: Take 5 for Safety
AGS Relay Fire – Lessons Learned
Quote of the Week – “If she weighs the same as a duck, she’s made of wood.” “And therefore…?” “A witch!” Monty Python
Collider-Accelerator Department
3-29-11

## Slide 2: AGS Relay Fire - Lessons Learned
Lesson Learned
  Pre-1970's wires used to power electromagnetic relays configured in stacks must be considered as flammable fuel loading near an ignition source
Events
  Fire damage to the first-floor Terminal Room near MCR; about 50 relays and associated wiring were damaged by fire; the relays and wiring were part of the AGS access controls system
  Past C-AD critiques associated with overheated relays did not recognize the use of non-flame retardant insulated wire in this older plant area
  Removal of known flammables such as Plexiglas covers were the focus of extent of condition reviews and corrective actions from these past events
  An overheated relay coil never resulted in igniting wiring insulation in the past
  Past fire hazards analyses and assessments by independent teams of outside fire-safety professionals did not identify wire insulation of this age as potentially flammable

## Slide 3: AGS Relay Fire - Lessons Learned
Analysis
  The root causal factor of this fire was the failure to identify the presence of non-flame retardant insulation on 120 V wiring connected to relays that were known to routinely operate at high temperatures and to occasionally fail and emit a flame
  The root cause was a failure to "see" beyond well known rule-based flammables such as Plexiglas and plastics, which resulted in the failure to inspect relay stacks for the presence of non-flame retardant wiring
  The insulation on wiring installed in the 1950s did not meet flammability standards first developed in the 1970s in the US
  The presence of this type of wiring was not known

## Slide 4: AGS Relay Fire - Lessons Learned
Recommended Actions
  Establish a project with milestones to remove unused cable and all wiring with potentially flammable insulation
  Add questions to the configuration management systems that address the flame retardant characteristics of legacy wiring when making modifications to the accelerator or experiments; add questions that address the hazards associated with use of electromechanical relays such as the potential to be ignition sources
  Evaluate the insulation on wiring in other relay rooms and replace wiring or disposition potential ignition sources
  Establish a program to identify and assess fire risk of potentially flammable wiring insulation in pre-1970 facilities or in facilities constructed with excess wiring from older construction projects
  Form a Legacy Hazard Committee with personnel who have decades of experience and extensive knowledge of operations and review all accelerator facilities for other legacy hazards

## Slide 5: Quote of the Week - Dedicated to all the continuous improvement specialists who draw incredible conclusions from amazing feats of data analysis… and then step back to let others do the implementation work
CROWD: A witch! A witch! A witch! We've got a witch! A witch!
VILLAGER #1: We have found a witch, might we burn her?
SIR BEDEMIR: How do you know she is a witch?
VILLAGER #2: She looks like one. She has got a wart.
CROWD: Burn! Burn her!
SIR BEDEMIR: Quiet. There are ways of telling if she’s a witch. Tell me, what do you do with witches?
CROWD: Burn, burn them up!
SIR BEDEMIR: And what do you burn apart from witches?
VILLAGER #2: Wood!
SIR BEDEMIR: So, why do witches burn?
VILLAGER #3: Because they're made of wood.
SIR BEDEMIR: Good! So, how do we tell whether she is made of wood? Does wood sink in water?
VILLAGER #1: No, no. It floats! It floats!
SIR BEDEMIR: What also floats in water?
KING ARTHUR: A duck.
SIR BEDEMIR: Exactly! So, logically...,
VILLAGER #1: If... she.. weighs the same as a duck, she's made of wood.
SIR BEDEMIR: And therefore--?
VILLAGER #1: A witch!
CROWD: A witch!
SIR BEDEMIR: We shall use my larger scales! …
Notes: Scene is old England; small village; a woman is pushed onto the knight’s podium by a crowd of villagers; the villagers put a cone shaped hat on the woman’s head and attached a long carrot to the end of her nose; they demand a decision from Sir Bedemir, a Knight of the Round Table
Related to management decisions